FORM I-B-8-1(1)

3.1	 Hydraulic Turbines- Technical Particulars

This is Technical Particulars of Turbine and Unit Auxiliary Equipment Units 1 and 2 (quantities are given per unit unless otherwise indicated)

The values shown as Specified* are mandatory and guaranteed. No deviations are permitted. In the event of conflict between the values given below and those required by the Technical Clauses the requirements of the Technical Clauses take precedence. Guaranteed values thus # are to be nominated by the Contractor

Other values and descriptions are provisional and may change during detail design with the prior approval of the Engineer.

| Ref No | ITEM | Unit | Specified* | Answer (or reference to answer) to query |
| --- | --- | --- | --- | --- |
| 1 | Turbine |  |  |  |
| .1 | Maker’s Name |  |  |  |
| .2 | Type |  | Kaplan* |  |
| .3 | Normal Speed | rpm | # |  |
| .4 | Maximum "on cam" runaway speed | rpm | # |  |
| .5 | maximum "off cam" runaway speed | rpm | # |  |
| .6 | Maximum load rejection speed | rpm | # |  |
| .7 | Direction of rotation viewed from above |  | Clockwise* |  |
| .8 | Flywheel effect GD2 (runner+shaft) | kgm2 | # |  |
| .9 | Flywheel effect H (runner+shaft) | kWs/kVA | # |  |
| .10 | Flywheel effect H (all rotating parts) to meet regulation guarantees | kWs/kVA | ≥3.817* |  |
| .11 | Design head | m | 25.66* |  |
| .12 | Rated head | m | 21* |  |
| .13 | Maximum load rejection head at spiral case centreline | m | ≤ 50* |  |
| .14 | Minimum head in draft tube cone during any transient | m | ≥ -5* |  |
| .15 | Rated output | MW | 103* |  |
| .16 | Design output | MW | # |  |
| .17 | Design flow at 25.66 m head | m3/s | # |  |
| .18 | Maximum flow at maximum head | m3/s | # |  |
| .19 | Maximum flow at "on cam" runaway speed | m3/s | # |  |
| .20 | Maximum flow at "off cam" runaway speed | m3/s | # |  |
| .21 | Rated flow at 21 m head | m3/s | # |  |
| .22 | Peak efficiency at design head | % | ≥ 95* |  |
| .23 | Weighted Efficiency | % | ≥ 93.0* |  |
| .24 | Efficiency drop between point of best efficiency and rated output | % | ≤ 1* |  |
| .25 | Total mechanical losses at rated speed | kW | # |  |
| .26 | Maximum hydraulic thrust | kN | # |  |
| .27 | Guide vane leakage when closed at 34.1 m head | m3/s | # |  |
| 2 | Turbine Model Test |  |  |  |
| .1 | Laboratory |  |  |  |
| .2 | Model runner diameter | mm | ≥ 300* |  |
| .3 | Model head for efficiency testing | m | ≥ 20* |  |
| .4 | Model head for cavitation testing | m | Froude No* |  |
| .5 | Model head for runaway speed testing | m | Froude No* |  |
| .6 | CFD Analysis computer programme |  | # |  |
| 3 | Site efficiency test (if required) |  |  |  |
| .1 | Name of agency who will conduct the test |  | # |  |
| .2 | Experience with the scintillation method |  | # |  |
| .3 | Tolerance on efficiency measurement | % | Standard IEC 90041* |  |
| 4 | Stay Ring |  |  |  |
| .1 | Outer diameter |  | # |  |
| .2 | Inner diameter |  | # |  |
| .3 | Thickness of upper ring plate |  | # |  |
| .4 | Thickness of lower ring plate |  | # |  |
| .5 | Width of stay vane |  | # |  |
| .6 | Length of stay vane |  | # |  |
| .7 | Thickness of stay vane |  | # |  |
| .8 | Number of segments for transport |  | # |  |
| .9 | Method of joining segments at site |  | # |  |
| .10 | Material of stay ring |  | # |  |
| .11 | Total weight stay ring |  | # |  |
| .12 | Maximum stress in stay ring |  | As specified* |  |
| 5 | Runner |  |  |  |
| .1 | Transport system to turbine pit (with intermediate top cover etc) |  | # |  |
| .2 | Where erected at site |  | # |  |
| .3 | Runner CL elevation | m | # |  |
| .4 | Tip diameter | m | # |  |
| .5 | No of blades |  | # |  |
| .6 | Minimum thickness of blades | mm | # |  |
| .7 | Surface finish of blades | m | # |  |
| .8 | Runner blade material |  | # |  |
| .9 | Runner hub material |  | # |  |
| .10 | Maximum stress in runner blade in normal operation | MPa | As specified* |  |
| .11 | Maximum stress in runner blade at load rejection | MPa | As specified* |  |
| .12 | Maximum stress in runner blade at "on cam" runaway | MPa | # |  |
| .13 | Cavitation guarantee |  | As specified* |  |
| .14 | Weight of completed runner | tonne | # |  |
| .15 | Weight of single runner blade | Kg | # |  |
| 6 | Runner blade actuation mechanism |  |  |  |
| .1 | Manufacturer of trunnion bearings |  | # |  |
| .2 | Type of trunnion bearings |  | # |  |
| .3 | Manufacturer of trunnion seals |  | # |  |
| 7 | Runner envelope |  |  |  |
| .1 | Clearance with runner tips | mm | # |  |
| .2 | Minimum thickness | mm | # |  |
| .3 | Number of delivered sections |  | # |  |
| .4 | Method of joining at site |  | # |  |
| .5 | Runner envelope material |  | # |  |
| .6 | Size of access door in runner envelope |  | # |  |
| .7 | Possible to remove runner blade through access opening |  | # |  |
| .8 | Feasibility of runner blade removal through access door |  | # |  |
| .9 | Cavitation guarantee |  | As specified* |  |
| .10 | Weight of runner envelope complete | kg |  |  |
| 8 | Throat Ring |  |  |  |
| .1 | Minimum thickness | mm | # |  |
| .2 | Number of delivered sections |  | # |  |
| .3 | Method of joining at site |  | # |  |
| .4 | Throat ring material |  | # |  |
| .5 | Cavitation guarantee |  | As specified* |  |
| .6 | Extent of stainless steel below runner | m | ≥ 1 |  |
| .7 | Weight of discharge ring complete | kg | # |  |
| .8 | Material of discharge ring |  | # |  |
| 9 | Outer top cover |  |  |  |
| .1 | Minimum thickness | mm | # |  |
| .2 | Number of delivered sections |  | # |  |
| .3 | Method of joining at site |  | # |  |
| .4 | Outer head cover material |  | # |  |
| .5 | Weight of outer top cover complete | kg | # |  |
| 10 | Intermediate top cover |  |  |  |
| 1 | Minimum thickness | mm | # |  |
| .2 | Number of delivered sections |  | # |  |
| .3 | Method of joining at site |  | # |  |
| .4 | Intermediate top cover material |  | # |  |
| .5 | Maximum stress in normal operation | MPa | As specified* |  |
| .6 | Maximum stress at load rejection | MPa | As specified* |  |
| .7 | Maximum stress at "on cam" runaway | MPa | # |  |
| .8 | Weight of intermediate top cover complete | kg | # |  |
| 11 | Inner top cover |  |  |  |
| .1 | Minimum thickness | mm | # |  |
| .2 | Inner top cover material |  | # |  |
| 12 | Thrust bearing cone (if applicable) |  |  |  |
| .1 | Minimum thickness | mm | # |  |
| .2 | Size of access opening width/height | mm | # |  |
| .3 | Thrust bearing cone material |  | # |  |
| .4 | Maximum stress in normal operation | MPa | As specified* |  |
| .5 | Maximum stress at load rejection | MPa | As specified* |  |
| .6 | Maximum stress at "on cam" runaway | MPa | # |  |
| .7 | Weight of thrust bearing cone complete | kg | # |  |
| 13 | Turbine Shaft |  |  |  |
| .1 | Method of construction |  | # |  |
| .2 | Minimum outside diameter | mm | # |  |
| .3 | Diameter of bore | mm | # |  |
| .4 | Diameter of flange at generator coupling | mm | # |  |
| .5 | Elevation of shaft coupling | m | # |  |
| .6 | Number and size of generator shaft coupling bolts |  | # |  |
| .7 | Number and size of runner coupling bolts |  | # |  |
| .8 | Turbine shaft material |  | # |  |
| .9 | Maximum stress in normal operation | MPa | As specified* |  |
| .10 | Maximum stress at load rejection | MPa | As specified* |  |
| .11 | maximum stress with generator short circuit | MPa | As specified* |  |
| .12 | Weight of turbine shaft | kg | # |  |
| 14 | Shaft service seal |  |  |  |
| .1 | Type of seal (together with details and precedence) |  | # |  |
| .2 | Manufacturer of seal |  | # |  |
| .3 | Diameter of seal | mm | # |  |
| .4 | Seal water flow | l/min | # |  |
| .5 | Manufacturer of hydrocyclone |  | # |  |
| .6 | Manufacturer of filter |  | # |  |
| .7 | Normal operating temperature | oC | # |  |
| .8 | Shaft seal runner material |  | # |  |
| .9 | Shaft seal pad material |  | # |  |
| .10 | Shaft seal pump capacity (if required) | l/min | # |  |
| .11 | Shaft seal pump motor capacity (if required) | l/min | # |  |
| 15 | Shaft maintenance seal |  |  |  |
| .1 | Type of seal |  | # |  |
| .2 | Manufacturer of seal |  | # |  |
| .3 | Material of seal |  | # |  |
| .4 | Method of seal application |  | # |  |
| 16 | Regulating gear bushes and pads |  |  |  |
| .1 | Number of servomotors |  | # |  |
| .2 | Where servomotor force reacted |  | # |  |
| .3 | Maker of self lubricating bushes |  | # |  |
| .4 | Type of self lubricating bushes (together with details and precedence) |  | # |  |
| .5 | Material of guide vane stem sleeve |  | # |  |
| .6 | Hardness of sleeve | HB | # |  |
| .7 | Method of sleeve fixing |  | # |  |
| .8 | Material of regulating ring sliding surface |  | # |  |
| .9 | Hardness of surface | HB | # |  |
| .10 | Material of bush seals |  | # |  |
| .11 | Maximum stress at shear pin breakage | MPa | As specified* |  |
| .12 | Weight of guide vane servomotor without oil | kg | # |  |
| 17 | Regulating ring |  |  |  |
| .1 | Type of manufacture |  | # |  |
| .2 | Regulating ring material |  | # |  |
| .3 | Maximum stress at shear pin breakage | MPa | As specified* |  |
| .4 | Number of segments for transport |  | # |  |
| .5 | Weight of each segment | kg | # |  |
| .6 | Method of joining at site |  | # |  |
| 18 | Regulating gear |  |  |  |
| .1 | Number of shear pins |  | # |  |
| .2 | Number of stiff pins |  | # |  |
| .3 | Type of friction device (together with details and precedence) |  | # |  |
| .4 | Regulating gear material |  | # |  |
| 19 | Guide vanes |  |  |  |
| .1 | Number of guide vanes |  | # |  |
| .2 | Guide vane Centre Line EL | m | 186.9* |  |
| .3 | Type of manufacture of guide vanes |  | # |  |
| .4 | Details of guide vane end seals (together with drawings and precedence) |  | # |  |
| .5 | Guide vane material |  | # |  |
| .6 | Maximum stress in normal operation | MPa | As specified* |  |
| .7 | Maximum stress at load rejection | MPa | As specified* |  |
| .8 | Maximum stress at "on cam" runaway | MPa | # |  |
| .9 | Maximum stress at shear pin breakage | MPa | As specified* |  |
| .10 | Weight of a single guide vane | kg | # |  |
| 20 | Turbine bearing |  |  |  |
| .1 | Type |  | # |  |
| .2 | Manufacturer |  | # |  |
| .3 | Diameter of bearing | mm | # |  |
| .4 | Number of pads |  | # |  |
| .5 | Maximum permissible oil temperature | oC | # |  |
| .6 | Maximum permissible bearing surface temperature | oC | # |  |
| .7 | Quantity of cooling water required | l/min | # |  |
| .8 | Self pumping |  | # |  |
| 21 | Draft tube |  |  |  |
| .1 | EL of lowest point of draft tube | m | 163* |  |
| .2 | El of invert of draft exit | m | 170.9* |  |
| .3 | Height of draft tube at exit | m | 10 |  |
| .4 | Exit width of draft tube (one side) | m | 11.75 |  |
| .5 | Distance from unit CL to end of draft tube | m | 38* |  |
| .6 | Diameter of draft tube refill line | mm | 500* |  |
| .7 | Diameter of draft tube air release line | mm | 300* |  |
| .8 | Draft tube liner material |  | # |  |
| 22 | Governor |  |  |  |
| 22.1 | Digital Governor |  |  |  |
| .1 | Makers name |  | # |  |
| .2 | Type of governor (together with details and precedence) |  | # |  |
| .3 | Dead time | Secs | ≤± 2 for 10% load change* |  |
| .4 | Dead band | % | ≤ 0.04* |  |
| .5 | Range of speed droop adjustment |  | # |  |
| .6 | Range of timing adjustment for opening stroke |  | # |  |
| .7 | Rang of timing adjustment for closing stroke |  | # |  |
| .8 | Method of prime speed detection (together with details) |  | Voltage transformer* |  |
| .9 | Method of back up speed detection and switching |  | Toothed wheel* |  |
| .10 | Location of feed back transducer for guide vane |  | # |  |
| .11 | Type of feed back transducer for guide vane |  | # |  |
| .12 | Location of feed back transducer for runner blade position |  | # |  |
| .13 | Type of feed back transducer for runner blade |  | # |  |
| 22.2 | Hydraulic actuator |  |  |  |
| .1 | Make of Electro-hydraulic control valve for guide vane |  | # |  |
| .2 | Make of Electro-hydraulic control valve for runner blade |  | # |  |
| 22.3 | Digital Governor panel |  |  |  |
| .1 | Location | m | EL 202 |  |
| .2 | Size l/w/h | mm | # |  |
| 22.4 | Governor pumping set |  |  |  |
| .1 | System operating pressure | kPa | ≤ 6400* |  |
| .2 | Capacity of each governor oil pump | l/min | # |  |
| .3 | Manufacturer of the governor pumps |  | # |  |
| .4 | No of pumps | 3 | # |  |
| .5 | Motor capacity | kW | # |  |
| .6 | Volume of oil sump | l | # |  |
| .7 | Dimensions of oil sump l/w/h | m | # |  |
| .8 | Location of pumps and oil sump | m | EL 190.0* |  |
| .9 | Minimum operating oil pressure | MPa | # |  |
| .10 | Quantity of cooling water required | l/min | # |  |
| .11 | Operating oil volume of normal accumulator | m3 | # |  |
| .12 | Number of opening and closing cycles possible with normal accumulator |  | 2 opening - 3 closing* |  |
| .13 | Operating oil volume of emergency accumulator | m3 | # |  |
| .14 | Number of closing cycles possible with emergency accumulator |  | 2 closing* |  |
| 22.5 | Governor Compressed air system |  |  |  |
| .1 | Location of governor compressed air system | m | EL 202* |  |
| .2 | Size required for governor compressor room (length/width/Height) | m | # |  |
| .3 | Compressor manufacturer |  | # |  |
| .4 | Type of Compressor |  | # |  |
| .5 | Dimensions of compressor (length/width/height) |  | # |  |
| .6 | Weight of compressor complete | kg | # |  |
| .7 | Capacity of compressor motor | kW | # |  |
| .8 | Compressor cooling system |  | Air* |  |
| .9 | Number of compressors (total for units 1 & 2) |  | 2* |  |
| .10 | System pressure | kPa | ≤ 6400 |  |
| .11 | Compressor capacity (Free air) | m3/min | # |  |
| .12 | No of air receivers |  | 1* |  |
| .13 | Dimensions of receiver for governor air compressor (dia/ht) | m | # |  |
| .14 | Volume of receiver | m3 | ≥ 0.5 |  |
| .15 | Weight of receiver | kg | # |  |
| .16 | Receiver material |  | # |  |
| 23 | Unit cooling system |  |  |  |
| 23.1 | Coarse automatic strainers |  |  |  |
| .1 | Maker's name |  | # |  |
| .2 | Maximum throughput of water | l/min | # |  |
| .3 | Pressure drop when clean |  | # |  |
| .4 | Sizes of basket mesh | mm | 1* |  |
| .5 | Design pressure | MPa | # |  |
| .6 | Test pressure | MPa | # |  |
| .7 | Basket material |  | # |  |
| .8 | Body material |  | # |  |
| 23.2 | Fine automatic strainers |  |  |  |
| .1 | Maker's name |  | # |  |
| .2 | Maximum throughput of water | l/min | # |  |
| .3 | Pressure drop when clean | MPa | # |  |
| .4 | Sizes of basket mesh | μm | 300* |  |
| .5 | Design pressure | kPa | # |  |
| .6 | Test pressure | kPa | # |  |
| .7 | Basket material |  | # |  |
| .8 | Body material |  | # |  |
| .9 | Weight of strainer | kg |  |  |
| 23.3 | Closed loop pumps |  |  |  |
| .1 | Number of pumps |  | 2 |  |
| .2 | Manufacturer |  | # |  |
| .3 | Rated head | m | # |  |
| .4 | Rated flow | l/min | # |  |
| .5 | Capacity of pump motor | kW | # |  |
| .6 | Pump discharge filter mesh size | μm | # |  |
| .7 | Weight of pump | kg | # |  |
| 23.4 | Raw water/closed loop water heat exhangers |  |  |  |
| .1 | Number |  | 3 |  |
| .2 | Manufacturer |  | # |  |
| .3 | Type |  | # |  |
| .4 | Raw water temperature in/out | oC | # |  |
| .5 | Closed loop temperature in/out | oC | # |  |
| .6 | Tube material |  | # |  |
| .7 | Shell material |  | # |  |
| .8 | Tube fouling factor |  | # |  |
| .9 | Weight of heat exchanger empty | kg | # |  |
| 23.5 | Raw water dosing system |  |  |  |
| .1 | Manufacturer |  | # |  |
| .2 | Chemicals used |  | # |  |
| .3 | Pump pressure | kPa | # |  |
| .4 | Pump flow | l/min | # |  |
| 23.6 | Closed loop water dosing system |  |  |  |
| .1 | Manufacturer |  | # |  |
| .2 | Chemicals used |  | # |  |
| .3 | Pump pressure | kPa | # |  |
| .4 | Pump flow | l/min | # |  |
| 23.7 | Expansion tank |  |  |  |
| .1 | Manufacturer |  | # |  |
| .2 | Type |  | # |  |
| .3 | Size l/w/h | mm | # |  |
| 23.8 | CW on/off valve |  |  |  |
| .1 | Manufacturer of motor operated unit CW control valve |  | # |  |
| .2 | Type of valve |  | Ball* |  |
| .3 | Size of CW valve | mm | # |  |
| 23.9 | Other CW valves |  |  |  |
| .1 | Ball valve manufacturer |  | # |  |
| .2 | Butterfly valve manufacturer |  | # |  |
| .3 | Non-return valve manufacturer |  | # |  |
| .4 | Gate valve manufacturer |  | # |  |
| 24 | Pipework and grills |  |  |  |
| .1 | Raw water piping material |  | # |  |
| .2 | Closed loop water piping material |  | # |  |
| .3 | Grill material |  | # |  |